## Sheet1
PLC Data Information
Data Read From PLC
Address | Data Type | Description
%MW1000 | INT | Current Day
%MW1001 | INT | Current Hour
%MW1002 | INT | Current Minute
%MW1003 | REAL | Weather Type Index (Sunny, Cloudy, Rainy)
%MW1004 | REAL | Water Tank Supply Pump 1 Speed (%)
%MW1006 | REAL | Water Tank Supply Pump 1 Flow (L/sec)
%MW1008 | REAL | Water Tank Supply Pump 1 Power (kW)
%MW1010 | REAL | Water Tank Supply Pump 2 Speed (%)
%MW1012 | REAL | Water Tank Supply Pump 2 Flow (L/sec)
%MW1014 | REAL | Water Tank Supply Pump 2 Power (kW)
%MW1016 | REAL | Water Tank Discharge Pump Speed (%)
%MW1018 | REAL | Water Tank Discharge Pump Flow (L/sec)
%MW1020 | REAL | Water Tank Discharge Pump Power (kW)
%MW1022 | REAL | Water Tank Level (kL)
%MW1024 | REAL | Real-time Total (All Pump) Power Usage at 15 minute interval (kW)
%MW1026 | REAL | Daily Total Accumulation of Power Usage (kW) for a 24 hour period- reset at midnight
%MW1028 | REAL | Real-time Solar Power Generation at 15 minute interval (kW)
%MW1030 | REAL | Daily Total Accumulation of Solar Generation (kW) for a 24 hour period- reset at midnight
%MW1032 | REAL | Real-time 15 minute Interval Temperature (°C)
%MW1034 | REAL | Daily Total Grid Power Consumption (kW) for a 24 hour period- reset at midnight
%MW1036 | BYTE | Pump Running Status Information (Bit 0= Water Supply Pump 1 Run/Stop Status, Bit 1= Water Supply Pump 2 Run/Stop Status, Bit 2= Water Discharge Pump Run/Stop Status)
Data Write To PLC
%MW500 | BYTE | Water Supply Pump Control ( Bit 0= Enable Remote Control (0-disable/ 1-enable), Bit 1= Water Supply pump 1 Run Request (0-off/ 1-on), Bit 2= Water Supply pump 2 Run Request (0-off/ 1-on)